## BuildingView
Project name | [10 empty] | Doc. version
Project number | [10 empty] | 2026-01-29
Building | Part | Zone no. | Name of zone | NV | Name of NVE Controller | Temp. | CO2 | Heating | Mech. ventilation | Sun shading | Special functions
1 | 1 | 1 | Zone 1 | X | NVE01.1 | X | X | - | - | - | Room sensor via BACnet IP (BMS)
1 | 1 | 2 | Zone 2 | X | NVE01.2 | X | X | - | - | - | Room sensor via BACnet IP (BMS)
1 | 1 | 3 | Zone 3 | X | NVE02.1 | x | x
1 | 1 | 4 | Zone 4 | X | NVE02.2 | x | x

## WCC-Info
MotorController name | WCC type | IP xxx.xxx.xxx.xxx | MAC xx:xx:xx:xx:xx:xx | BACnet Device ID | BACnet MAC address | KNX physical address | Modbus slave address | Placed
WCC01 | WCC 320 P 1012 U4 | 10.20.30.61 | F4:B3:81:02:xx:xx | 55001 |  |  |  | Basement
WCC02 | WCC 320 P 1012 U4 | 10.20.30.62 | F4:B3:81:02:xx:xx | 55002 |  |  |  | Basement

## BACnetExchangeList
Exchange | Unit | Zone | Name of zone/room | NVE Controller | Remarks | Re-Send | ID | Object Name | Device ID
From BMS to MotorController (WCC), [BACnet WRITE] signals
WCC01 | [8 empty] | 55001
Rain | Bool |  | Outdoor | - | 0=No rain / 1=Rain | Min. 10 min or change | BV1 | Connection_1 | 55001
Set the building mode |  |  |  |  | 0=Occupied 1=Unoccupied 2=Secured |  | AV45 | Building_mode | 55001
Manual override (30 min.) | % | 1 | Zone 1 | NVE01.1 | Open: 100 Close: -100 Stop: 0 |  | AV11 | Hand_relative_position_motor_group_1 | 55001
Manual override (30 min.) | % | 2 | Zone 2 | NVE01.2 | Open: 100 Close: -100 Stop: 0 |  | AV12 | Hand_relative_position_motor_group_2 | 55001
Actual room temperature | °C | 1 | Zone 1 | NVE01.1 |  | Min. 10 min or change | AV66 | Temperature_NV_controller_1 | 55001
Actual room temperature | °C | 2 | Zone 2 | NVE01.2 |  | Min. 10 min or change | AV67 | Temperature_NV_controller_2 | 55001
Actual CO2 level in room | ppm | 1 | Zone 1 | NVE01.1 |  | Min. 10 min or change | AV76 | CO2_NV_controller_1 | 55001
Actual CO2 level in room | ppm | 2 | Zone 2 | NVE01.2 |  | Min. 10 min or change | AV77 | CO2_NV_controller_2 | 55001
Actual relative humidity level in room | % | 1 | Zone 1 | NVE01.1 |  | Min. 10 min or change | AV86 | Relative_humidity_NV_controller_1 | 55001
Actual relative humidity level in room | % | 2 | Zone 2 | NVE01.2 |  | Min. 10 min or change | AV87 | Relative_humidity_NV_controller_2 | 55001
Base temperature setpoint in room | °C | 1 | Zone 1 | NVE01.1 | 21°C | Min. 10 min or change | AV106 | NV_base_temperature_setpoint_NV_controller_1 | 55001
Base temperature setpoint in room | °C | 2 | Zone 2 | NVE01.2 | 21°C | Min. 10 min or change | AV107 | NV_base_temperature_setpoint_NV_controller_2 | 55001
Night offset temperature in NV controller | °C | 1 | Zone 1 | NVE01.1 |  | Min. 10 min or change | AV156 | NV_cooling_night_offset_NV_controller_1 | 55001
Night offset temperature in NV controller | °C | 2 | Zone 2 | NVE01.2 |  | Min. 10 min or change | AV157 | NV_cooling_night_offset_NV_controller_2 | 55001
Enable/Disable Winter mode NV in room |  | 1 | Zone 1 | NVE01.1 | Enable = 1 / Disable = 0 |  | BO31 | NV_Force_winter_1 | 55001
Enable/Disable Winter mode NV in room |  | 2 | Zone 2 | NVE01.2 | Enable = 1 / Disable = 0 |  | BO32 | NV_Force_winter_2 | 55001
Pulse ventilation (Morning) |  | 1 | Zone 1 | NVE01.1 | First = 0 (Reset) Second = 1 (Activate) |  | BO41 | NV_Ventilate_1 | 55001
Pulse ventilation (Morning) |  | 2 | Zone 2 | NVE01.2 | First = 0 (Reset) Second = 1 (Activate) |  | BO42 | NV_Ventilate_2 | 55001
Enable/Disable Night in room |  | 1 | Zone 1 | NVE01.1 | Enable = 1 / Disable = 0 |  | BO61 | NV_Night_1 | 55001
Enable/Disable Night in room |  | 2 | Zone 2 | NVE01.2 | Enable = 1 / Disable = 0 |  | BO62 | NV_Night_2 | 55001
Outdoor temperature | °C | 1 | Zone 1 | NVE01.1 |  |  | AV96 | Outdoor_temperature_in_NV_controller_1 | 55001
Outdoor temperature | °C | 2 | Zone 2 | NVE01.2 |  |  | AV97 | Outdoor_temperature_in_NV_controller_2 | 55001
Set the wind speed, used for safety | m/s |  | Outdoor |  | Wind speed | Min. 10 min or change | AV41 | Wind speed | 55001
Set the filtered wind speed, use for NV | m/s |  | Outdoor |  | Wind speed filtered | Min. 10 min or change | AV42 | Wind speed filtered | 55001
Set the wind direction | 0-359° |  | Outdoor |  | Wind direction | Min. 10 min or change | AV43 | Wind direction | 55001
Set the filtered wind direction, used for NV | 0-359° |  | Outdoor |  | Wind direction filtered | Min. 10 min or change | AV44 | Wind direction filtered | 55001
WCC02 | [8 empty] | 55002
Rain | Bool |  | Outdoor | - | 0=No rain / 1=Rain | Min. 10 min or change | BV1 | Connection_1 | 55002
Set the building mode |  |  |  |  | 0=Occupied 1=Unoccupied 2=Secured |  | AV45 | Building_mode | 55002
Override windows from LCD Display (30 min.) | % | 3 | Zone 3 | NVE02.1 | Open: 100 Close: -100 Stop: 0 |  | AV11 | Hand_relative_position_motor_group_1 | 55002
Override windows from LCD Display (30 min.) | % | 4 | Zone 4 | NVE02.2 | Open: 100 Close: -100 Stop: 0 |  | AV12 | Hand_relative_position_motor_group_2 | 55002
Override windows from LCD Display (30 min.) | % | 3 | Zone 3 | NVE02.1 | Open: 100 Close: -100 Stop: 0 |  | AV13 | Hand_relative_position_motor_group_3 | 55002
Override windows from LCD Display (30 min.) | % | 4 | Zone 4 | NVE02.2 | Open: 100 Close: -100 Stop: 0 | Stair Bottom Stair lvl 2 Stair lvl 3 | AV14 AV15 AV16 | Hand_relative_position_motor_group_4 Hand_relative_position_motor_group_5 Hand_relative_position_motor_group_6 | 55002
Actual room temperature | °C | 3 | Zone 3 | NVE02.1 |  | Min. 10 min or change | AV66 | Temperature_NV_controller_1 | 55002
Actual room temperature | °C | 4 | Zone 4 | NVE02.2 |  | Min. 10 min or change | AV67 | Temperature_NV_controller_2 | 55002
Actual CO2 level in room | ppm | 3 | Zone 3 | NVE02.1 |  | Min. 10 min or change | AV76 | CO2_NV_controller_1 | 55002
Actual CO2 level in room | ppm | 4 | Zone 4 | NVE02.2 |  | Min. 10 min or change | AV77 | CO2_NV_controller_2 | 55002
Actual relative humidity level in room | % | 3 | Zone 3 | NVE02.1 |  | Min. 10 min or change | AV86 | Relative_humidity_NV_controller_1 | 55002
Actual relative humidity level in room | % | 4 | Zone 4 | NVE02.2 |  | Min. 10 min or change | AV87 | Relative_humidity_NV_controller_2 | 55002
Base temperature setpoint in room | °C | 3 | Zone 3 | NVE02.1 |  | Min. 10 min or change | AV106 | NV_base_temperature_setpoint_NV_controller_1 | 55002
Base temperature setpoint in room | °C | 4 | Zone 4 | NVE02.2 |  | Min. 10 min or change | AV107 | NV_base_temperature_setpoint_NV_controller_2 | 55002
Night offset temperature in NV controller | °C | 3 | Zone 3 | NVE02.1 |  | Min. 10 min or change | AV156 | NV_cooling_night_offset_NV_controller_1 | 55002
Night offset temperature in NV controller | °C | 4 | Zone 4 | NVE02.2 |  | Min. 10 min or change | AV157 | NV_cooling_night_offset_NV_controller_2 | 55002
Enable/Disable Winter mode NV in room |  | 3 | Zone 3 | NVE02.1 | Enable = 1 / Disable = 0 |  | BO31 | NV_Force_winter_1 | 55002
Enable/Disable Winter mode NV in room |  | 4 | Zone 4 | NVE02.2 | Enable = 1 / Disable = 0 |  | BO32 | NV_Force_winter_2 | 55002
Pulse ventilation (Morning) |  | 3 | Zone 3 | NVE02.1 | First = 0 (Reset) Second = 1 (Activate) |  | BO41 | NV_Ventilate_1 | 55002
Pulse ventilation (Morning) |  | 4 | Zone 4 | NVE02.2 | First = 0 (Reset) Second = 1 (Activate) |  | BO42 | NV_Ventilate_2 | 55002
Enable/Disable Night in room |  | 3 | Zone 3 | NVE02.1 | Enable = 1 / Disable = 0 |  | BO61 | NV_Night_1 | 55002
Enable/Disable Night in room |  | 4 | Zone 4 | NVE02.2 | Enable = 1 / Disable = 0 |  | BO62 | NV_Night_2 | 55002
Outdoor temperature | °C | 3 | Zone 3 | NVE02.1 |  | Min. 10 min or change | AV96 | Outdoor_temperature_in_NV_controller_1 | 55002
Outdoor temperature | °C | 4 | Zone 4 | NVE02.2 |  | Min. 10 min or change | AV97 | Outdoor_temperature_in_NV_controller_2 | 55002
From MotorController (WCC) to BMS, [BACnet READ] signals
WCC01 | [8 empty] | 55001
MotorController error status |  |  | Basement | - |  |  | BI41 | Error_system | 55001
One or more NV controllers has an error |  |  | Basement | - |  |  | BI42 | Error_nv_controllers | 55001
NV Controller status |  | 1 | Zone 1 | NVE01.1 |  |  | BI75 | NV_Error_status_1 | 55001
NV Controller status |  | 2 | Zone 2 | NVE01.2 |  |  | BI76 | NV_Error_status_2 | 55001
Actual position window | % | 1 | Zone 1 | NVE01.1 |  |  | AI3 | Actual_position_motor_line_S2_X1 | 55001
Actual position window | % | 1 | Zone 1 | NVE01.1 |  |  | AI4 | Actual_position_motor_line_S2_X2 | 55001
Actual position window | % | 1 | Zone 1 | NVE01.1 |  |  | AI5 | Actual_position_motor_line_S2_X3 | 55001
Actual position window | % | 2 | Zone 2 | NVE01.2 |  |  | AI7 | Actual_position_motor_line_S2_X5 | 55001
Actual position window | % | 2 | Zone 2 | NVE01.2 |  |  | AI8 | Actual_position_motor_line_S2_X6 | 55001
Actual position window | % | 2 | Zone 2 | NVE01.2 |  |  | AI9 | Actual_position_motor_line_S2_X7 | 55001
Actual MAX position window | % | 1 | Zone 1 | NVE01.1 |  |  | AI13 | Actual_max_position_motor_line_S2_X1 | 55001
Actual MAX position window | % | 1 | Zone 1 | NVE01.1 |  |  | AI14 | Actual_max_position_motor_line_S2_X2 | 55001
Actual MAX position window | % | 1 | Zone 1 | NVE01.1 |  |  | AI15 | Actual_max_position_motor_line_S2_X3 | 55001
Actual MAX position window | % | 2 | Zone 2 | NVE01.2 |  |  | AI17 | Actual_max_position_motor_line_S2_X5 | 55001
Actual MAX position window | % | 2 | Zone 2 | NVE01.2 |  |  | AI18 | Actual_max_position_motor_line_S2_X6 | 55001
Actual MAX position window | % | 2 | Zone 2 | NVE01.2 |  |  | AI19 | Actual_max_position_motor_line_S2_X7 | 55001
Manual override activated | Bit 15: 1 | 1 | Zone 1 | NVE01.1 | S2_X1-3 in same MG |  | BS13 | Status_motor_line_S2_X1 | 55001
Manual override activated | Bit 15: 1 | 2 | Zone 2 | NVE01.2 | S2_X5-7 in same MG |  | BS17 | Status_motor_line_S2_X5 | 55001
The motor line calls for service | Bit 27: 1 | 1 | Zone 1 | NVE01.1 |  |  | BS13 | Status_motor_line_S2_X1 | 55001
The motor line calls for service | Bit 27: 1 | 1 | Zone 1 | NVE01.1 |  |  | BS14 | Status_motor_line_S2_X2 | 55001
The motor line calls for service | Bit 27: 1 | 1 | Zone 1 | NVE01.1 |  |  | BS15 | Status_motor_line_S2_X3 | 55001
The motor line calls for service | Bit 27: 1 | 2 | Zone 2 | NVE01.2 |  |  | BS17 | Status_motor_line_S2_X5 | 55001
The motor line calls for service | Bit 27: 1 | 2 | Zone 2 | NVE01.2 |  |  | BS18 | Status_motor_line_S2_X6 | 55001
The motor line calls for service | Bit 27: 1 | 2 | Zone 2 | NVE01.2 |  |  | BS19 | Status_motor_line_S2_X7 | 55001
WCC02 | [8 empty] | 55002
MotorController error status |  |  | Basement | - |  |  | BI41 | Error_system | 55002
One or more NV controllers has an error |  |  | Basement | - |  |  | BI42 | Error_nv_controllers | 55002
NV Controller status |  | 3 | Zone 3 | NVE02.1 |  |  | BI75 | NV_Error_status_1 | 55002
NV Controller status |  | 4 | Zone 4 | NVE02.2 |  |  | BI76 | NV_Error_status_2 | 55002
Actual position window | % | 3 | Zone 3 | NVE02.1 |  |  | AI1 | Actual_position_motor_line_S1_X1 | 55002
Actual position window | % | 3 | Zone 3 | NVE02.1 |  |  | AI3 | Actual_position_motor_line_S2_X1 | 55002
Actual position window | % | 3 | Zone 3 | NVE02.1 |  |  | AI4 | Actual_position_motor_line_S2_X2 | 55002
Actual position window | % | 3 | Zone 3 | NVE02.1 |  |  | AI5 | Actual_position_motor_line_S2_X3 | 55002
Actual position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI6 | Actual_position_motor_line_S2_X4 | 55002
Actual position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI7 | Actual_position_motor_line_S2_X5 | 55002
Actual position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI8 | Actual_position_motor_line_S2_X6 | 55002
Actual position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI9 | Actual_position_motor_line_S2_X7 | 55002
Actual position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI10 | Actual_position_motor_line_S2_X8 | 55002
Actual MAX position window | % | 3 | Zone 3 | NVE02.1 |  |  | AI12 | Actual_max_position_motor_line_S1_X2 | 55002
Actual MAX position window | % | 3 | Zone 3 | NVE02.1 |  |  | AI13 | Actual_max_position_motor_line_S2_X1 | 55002
Actual MAX position window | % | 3 | Zone 3 | NVE02.1 |  |  | AI14 | Actual_max_position_motor_line_S2_X2 | 55002
Actual MAX position window | % | 3 | Zone 3 | NVE02.1 |  |  | AI15 | Actual_max_position_motor_line_S2_X3 | 55002
Actual MAX position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI16 | Actual_max_position_motor_line_S2_X4 | 55002
Actual MAX position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI17 | Actual_max_position_motor_line_S2_X5 | 55002
Actual MAX position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI18 | Actual_max_position_motor_line_S2_X6 | 55002
Actual MAX position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI19 | Actual_max_position_motor_line_S2_X7 | 55002
Actual MAX position window | % | 4 | Zone 4 | NVE02.2 |  |  | AI20 | Actual_max_position_motor_line_S2_X8 | 55002
Manual override activated | Bit 15: 1 | 3 | Zone 3 | NVE02.1 |  |  | BS11 | Status_motor_line_S1_X1 | 55002
Manual override activated | Bit 15: 1 | 3 | Zone 3 | NVE02.1 |  |  | BS13 | Status_motor_line_S2_X1 | 55002
Manual override activated | Bit 15: 1 | 4 | Zone 4 | NVE02.2 | S2_X2-3 in same MG |  | BS14 | Status_motor_line_S2_X2 | 55002
The motor line calls for service | Bit 27: 1 | 3 | Zone 3 | NVE02.1 |  |  | BS12 | Status_motor_line_S1_X2 | 55002
The motor line calls for service | Bit 27: 1 | 3 | Zone 3 | NVE02.1 |  |  | BS13 | Status_motor_line_S2_X1 | 55002
The motor line calls for service | Bit 27: 1 | 3 | Zone 3 | NVE02.1 |  |  | BS14 | Status_motor_line_S2_X2 | 55002
The motor line calls for service | Bit 27: 1 | 3 | Zone 3 | NVE02.1 |  |  | BS15 | Status_motor_line_S2_X3 | 55002
The motor line calls for service | Bit 27: 1 | 4 | Zone 4 | NVE02.2 |  |  | BS16 | Status_motor_line_S2_X4 | 55002
The motor line calls for service | Bit 27: 1 | 4 | Zone 4 | NVE02.2 |  |  | BS17 | Status_motor_line_S2_X5 | 55002
The motor line calls for service | Bit 27: 1 | 4 | Zone 4 | NVE02.2 |  |  | BS18 | Status_motor_line_S2_X6 | 55002
The motor line calls for service | Bit 27: 1 | 4 | Zone 4 | NVE02.2 |  |  | BS19 | Status_motor_line_S2_X7 | 55002
The motor line calls for service | Bit 27: 1 | 4 | Zone 4 | NVE02.2 |  |  | BS20 | Status_motor_line_S2_X8 | 55002